## Table 1
TITAN
®
"Y" (WYE) STRAINER f ANSI CLASS 125
CAST BRONZE f THREADED AND SOLDER ENDS
YS5556-0315
TITAN FLOW CONTROL, INC.
1 " YS 56 - BZ
MODELS: YS 55-BZ
( T h R E A d E d E N d S - B Ro N Z E)
YS 56-BZ
( S o L d E R E N d S - B Ro N Z E)
1 " YS 55 - BZ
FE AFT URES
s L A R g E S T R A ining c A pAci T Y
SIZE RANGE : 1 / 4 " ~ 3 "
TECTHNICAL
PRESSURE/ TEMPERATURE RATING (1)
w I T h I T S L A R G E B ody A N d S I Z A B L E S T R A I N I N G E L E M E N T, T h E y S 55 A N d y S 56
P Rov I d E E x C E L L E N T o P E N A R E A R AT I o S T h AT A R E T y P I C A L Ly T wo- A N d- A- h A L f T I M E S L A R G E R T h A N T h E C o R R E S P o N d I N G P I P E L I N E, M I N I M I Z I N G P R E S S U R E d Ro P AC Ro S S T h E vA Lv E.
s p R E ci S i O n m Ac H in E D S E AT S
P R E C I S I o N M AC h I N E d S C R E E N S E AT S I N B oT h T h E B ody A N d C A P h E L P To E N S U R E AC C U R AT E P o S I T I o N I N G of T h E S C R E E N d U R I N G R E A S S E M B Ly A f T E R C L E A N I N G. A L S o, T h E M AC h I N E d B ody S E AT S E N A B L E f I N E R f I LT R AT I o N B y P R E v E N T I N G d E B R I S B y PA S S.
s S E L f- c L E A ning c A pA B i L i T Y
w I T h A TA P P E d N P T B L ow- off C o N N E C T I o N, T h I S U N I T C A N B E f I T T E d w I T h A B L ow- dow N vA Lv E wh I C h fAC I L I TAT E S C L E A N I N G of T h E S T R A I N I N G E L E M E N T. P L E A S E C o N TAC T fAC To Ry fo R M o R E I N fo R M AT I o N.
s T H R E A D E D c A p
T I TA N' S y S 55 A N d y S 56 h Av E S T R A I G h T T h R E A d S To P E R M I T E A S y C A P R E M ovA L fo R C L E A N I N G A N d P Ro P E R A L I G N M E N T wh E N R E A S S E M B L I N G S T R A I N E R.
BZ - C84400 - ASTM B584 - CLASS 125
YS 55-BZ (THREADED)
WOG (Non-shock): 200 PSI @ 150 °F
PRESSURE/ TEMPERATURE RATING (1) BZ - C84400 - ASTM B584 - CLASS 125 YS 56-BZ (SOLDER) (2)
WOG (Non-shock):
400 PSI @ 100 °F (1/4" - 1 1/2")
315 PSI @ 100 °F (2" - 3")
1. The above listed temperatures are theoretical and may vary during actual operating conditions.
2. The internal working pressure rating for a solder joint strainer is dependent, not only on the strainer, but also on the composition of the solder used for the joint. The working pressure ratings shown for model YS 56-BZ (Solder) are representative of using an alloy Sb5 95-5 tin-antimony solder. For other solder joints, please consult factory.
g E n E R A L A p p L ic AT i O n: y- S T R A I N E R S A R E I N S TA L L E d I N A P I P I N G S y S T E M To R E M ov E U N wA N T E d d E B R I S f Ro M T h E
P I P E L I N E, P RoT E C T I N G E x P E N S I v E E q U I P M E N T dow N S T R E A M S U C h A S P U M P S, M E T E R S, S P R Ay N o Z Z L E S, C o M P R E S S o R S, A N d T U R B I N E S. T h E y C A N B E P L AC E d I N A ho R I Z o N TA L o R v E RT I C A L P I P E L I N E A S L o N G A S T h E S C R E E N I S I N A dow N wA R d P o S I T I o N. S T R A I N I N G I S AC C o M P L I S h E d v I A A N I N T E R N A L P E R fo R AT E d o R M E S h L I N E d S T R A I N I N G E L E M E N T, T h E S I Z E of wh I C h S ho U L d B E d E T E R M I N E d B A S E d o N T h E S I Z E of T h E S M A L L E S T PA RT I C L E To B E R E M ov E d.
S E Rvicing: T h E S T R A I N I N G E L E M E N T N E E d S R E G U L A R C L E A N I N G To P R E v E N T d E B R I S B U I L d U P. I T I S N oT A dv I S A B L E To
A L L ow T h E d I ff E R E N T I A L P R E S S U R E To I N C R E A S E B y 20 P S I . A LT ho U G h C L E A N I N G N o R M A L Ly R E q U I R E S T h E R E M ovA L of T h E S T R A I N I N G E L E M E N T, I N S TA L L I N G A N d U S I N G A T I TA N B L ow- off d R A I N vA Lv E C A N I N C R E A S E T h E T I M E B E T w E E N C L E A N I N G S.
The above data represents common market and service applications. No representation or guarantee, expressed or implied, i s g i ven due to the numerous var iations of concentrations, temperatures and f l ow conditions that may occur during actual service .
TITAN FLOW CONTROL, INC.
YOUR PIPELINE TO THE FUTURE!
Tel: 910-735-0000 s Fax: 910-738-3848 s titan@titanfci.com s www.titanfci.com 290 Corporate Drive s PO Box 7408 s Lumberton, NC 28358
YS5556-0315
TITAN
TITAN FLOW CONTROL, Inc.
290 Corporate Drive E-mail: titan@titanfci.com Lumberton, NC 28358 Web: www.titanfci.com
® Tel: 910.735.0000 Fax: 910.738.3848
"Y" (WYE) STRAINER
YS 55-BZ - (Threaded) YS 56-BZ - (Solder)
Threaded or Solder Ends • ANSI Class 125 • Bronze
ANSI Class
125
No. PART YS 55/56 - BZ
Bronze (C84400)
Illustrations are representative of YS 55-BZ (Threaded-end connections) only. Materials, as listed to the left, and Dimensions and Performance Data, as listed below, include both the YS 55- BZ and the YS 56-BZ (Solder-end connections). Please ask for certified drawings when required.
A
BILL OF MATERIALS (1)
1 Body Bronze (C84400) ASTM B584
2 Cap
ASTM B584
3 Straining Element (2) Stainless Steel
B
4 Gasket (2) Teflon
1. Bill of Materials represents standard materials. Equivalent or better materials may be substituted at the manufacturer's discretion.
2. Denotes recommended spare parts.
1
3
4
1.5" YS 55-BZ
Threaded Ends
5 D
5 NPT Plug (Blow-off) Bronze (C84400) ASTM B584
DIMENSIONS AND PERFORMANCE DATA (1)
SIZE |  | in 1/4 3/8 1/2 3/4 1 1 1/4 1 1/2 2 2 1/2 3
mm 8 10 15 20 25 32 40 50 65 80
A DIMENSION FACE TO FACE (YS 55) (2) A DIMENSION FACE TO FACE (YS 56) (2) B DIMENSION CENTER LINE TO BOTTOM (YS 55) B DIMENSION CENTER LINE TO BOTTOM (YS 56) C DIMENSION SCREEN REMOVAL D NPT Plug BLOW-OFF ASSEMBLEDWEIGHT YS 55- THREADED (APPROXIMATE) ASSEMBLEDWEIGHT YS 56 - SOLDER (APPROXIMATE) |  | in C/F 2.38 2.80 3.18 3.70 4.41 4.93 5.91 C/F 10.60
mm C/F 61 71 81 94 112 125 150 C/F 269
in C/F C/F 2.75 3.36 3.80 4.58 5.33 6.11 C/F 11.40
mm C/F C/F 70 86 97 116 136 155 C/F 290
in C/F 1.39 1.60 1.86 2.13 2.50 2.92 3.60 C/F 5.50
mm C/F 36 41 48 54 64 74 92 C/F 140
in C/F C/F 1.60 1.86 2.13 2.50 2.92 3.60 C/F 7.0
mm C/F C/F 41 48 54 64 74 92 C/F 140
in C/F 3.75 4.0 4.25 4.75 6.0 7.0 8.0 C/F 10.0
mm C/F 95 102 108 121 152 178 203 C/F 254
in C/F 1/4" 1/4" 1/4" 1/2" 1/2" 3/4" 1" C/F 1"
mm C/F 8 8 8 15 15 20 25 C/F 25
lb C/F 0.35 0.45 0.85 1.30 2.00 2.65 4.30 C/F 12.90
kg C/F 0.16 0.21 0.39 0.6 0.91 1.21 1.95 C/F 5.85
lb C/F C/F 0.35 0.55 0.85 1.60 1.65 2.80 C/F 16.20
kg C/F C/F 0.16 0.25 0.39 0.73 0.75 1.27 C/F 7.35
Flow Coefficient |  | Cv 0.7 2 8 15 22 38 42 70 110 160
1. Dimensions and weights are for reference only. When required, request certified drawings.
2. Face to face values have a tolerance of ±0.06 in (±2.0 mm).
pRESSURE - TEmpERATURE RATing - YS 55-BZ (Threaded)
(1/4" - 3")
PRESSURE - TEMPERATURE RATINGS (1)
SOURCE: ASME/ANSI B16.15
WOG (Non-shock): 200 PSI @ 150 °F
pRESSURE - TEmpERATURE RATing - YS 56-BZ (Solder) (1)
(1/4" - 1 1/2") (2" - 3")
WOG (Non-shock): 400 PSI @ 100 °F 315 PSI @ 100 °F
STAnDARD ScREEn SELEcTiOnS
250
200
150
100
Bronze (C84400) - ASTM B584 ANSI 125
Threaded Ends - YS 55
Size | Liquid |  | Open Area | Steam | Open Area
1/4" ~ 2" | 20 mesh |  | 51.8% | 30 mesh | 44.8%
2 1/2" ~ 3" | 1/16 (.0625) |  | 41% | 3/64 (.045) | 36%
REFERENCED STANDARDS & CODES
CODE DESCRIPTION
50
0
-20 100 200 300 400
Temperature (°F)
ASME/ANSI B16.18 Cast Copper Alloy Solder Joint Pressure Fittings
1. The pressure-temperature ratings given are ONLY for the YS 55-BZ (Threaded) per ASME B16.15. The internal working pressure rating for a solder joint strainer is dependent, not only on the strainer, but also on the composition of the solder used for the joint. The working pressure ratings shown for model YS 56-BZ (Solder) are representative of using an alloy Sb5 95-5
tin-antimony solder. For other solder joints, please consult factory.
ASME/ANSI B16.15 Cast Bronze Threaded Fittings
ASME/ANSI B16.50 Copper Alloy Braze-Joint Pressure Fittings
Titan FCI makes every effort to ensure the information presented on our literature accurately reflects exact product specifications. However, as product changes occur, there may be short-term differences between actual product specifications and the information contained within our literature. Titan FCI reserves the right to make design and specification changes to improve our products without prior notification. When required, request certified drawings.